## Cover
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
SHORT CIRCUIT CURRENT CALCULATION
1 | DG POWER Revised | L.X.ZHU |  |  | J.M.BYEON | 2025-04-04
0 | ISSUED FOR APPROVAL | L.X.ZHU | - | - | J.M.BYEON | 2024-09-30
Issue | DESCRIPTION | PREP'D | CHK'D | APPR'D | APPR'D | Date
SHORT-CIRCUIT CURRENT CALCULATION |  | CLASS
DRAWING NO.
|  | PROJECT NO. |  | YZJ 2022-1487
Seonam Office, 223, Sapyeong-ro, Nam-gu, Ulsan, Korea FAX. (052) 203-8800 (DESIGN), 202-8300(A/S) TEX. (052) 203-8860~78 (DESIGN), 202-8993(A/S)

## table
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
TABLE OF CONTENTS
| 1. | GENERAL | 3
| 1.1 | Scope | 3
| 1.2 | Standard Compliance and Reference Documents | 3
| 1.3 | Technology Index | 3
| 1.4 | Electrical System Data | 6
| 2. | SHORT CIRCUIT CALCULATION | 8
| 2.1 | Case Study | 8
| 2.2 | Result Summary | 9
| 2.6 | [6.6kV MAIN SWBD] NO.1 FWD TR PANEL | 23
| 2.7 | [6.6kV MAIN SWBD] NO.1 MAIN TR PANEL | 25
| ATTACHMENT |  | 12
| A | Simulation Diagram
| B | Simulation Output Data

## GENERAL
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
1. | GENERAL
1.1 | Scope
This report is aims to describe the results of short circuit current calculation for YZJ2022-1487 project in
details.This short circuit calculation will be used for the short circuit rating of all electrical equipment.
1.2 | Standard Compliance and Reference Documents
1.2.1 | The short circuit calculation method is used by ETAP software adheres to the requirements of IEC
"Short-circuit currents in three phase a.c. system”, as listed below.
| Standard | Title
| IEC 61363 | Electrical installations of ships and mobile and fixed offshore units
| IEC 60947 | Low voltage switchgear and controlgear
| IEC 62271 | High-voltage switchgear and controlgear
| IEC 60282 | High-voltage fuses
1.3 | Technology Index
In IEC short-circuit calculations; an equivalent voltage source at the fault location replaces all voltage sources.
A voltage factor “C” is applied to adjust the value of the equivalent voltage source for minimum and maximum
current calculations.
All machines are represented by their internal impedances. Transformer taps can be set at either the
nominal position or at the tapped position. System impedances are assumed to be balanced 3-phase,
and the method of symmetrical components is used for unbalanced fault calculations. Calculations
consider electrical distance from the fault location to synchronous generators. For a far-from-generator
fault, calculations assume that the steady-state value of the short circuit current is equal to the initial
symmetrical short circuit current.
1) | Transformer impedance
The equivalent series impedance Z= R + j X, in Ohm or %, at rated frequency and reference
temperature, across the terminals of one winding of pair, when the terminals of the other winding are
short-circuited and further winding, if existing, are open-circuited. For a three-phase transformer the
impedance is express as phase impedance. In a transformer having a tapped winding, the short-
circuit impedance is referred to a particular tap. Unless otherwise specified the principal tap applies.
2) | Rated Power
A conventional value of apparent power assigned to a winding which, together with the rated voltage
of the winding, determines its rates current.
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
3) | Rated Voltage
The voltage assigned to be applied, or developed at no-load, between the terminals of an untapped
winding, or of a tapped winding connected on the principal tapping. For a three-phase winding, it is
the voltage between line terminals.
4) | Rated Current
The Current flowing through a line terminal of a winding which is a derived from rated power and rated
voltage for the winding
5) | Tap
In a transformer having a tapped winding, a specific connection of that winding, representing a define
effective number of turns in the tapped winding and consequently a definite turns ratio between this
winding and any other winding with fixed number of turns. One of the tap is the principal tap and other
taps are described in relation to the principal tap by their respective tap factors.
6) | Xd”
This is the direct-axis sub transient reactance in percent.
7) | Xd’
This is the direct-axis transient synchronous reactance in percent.
8) | Xd
This is the direct-axis synchronous reactance in percent.
9) | Ist/In
Motor starting current, expressed as % of rated current
10) | Short Circuit
Accidental or intentional conductive path between two or more conductive parts forcing the electric potential
differences between these conductive parts to be equal or close to zero
11) | Initial Symmetrical Short Circuit Current (I”k)
The r.m.s value of the AC symmetrical component of an available short circuit current, applicable at the
instant of short circuit if the impedance remains at zero time value
12) | Peak Short Circuit Current (Ip)
Maximum possible instantaneous value of the available short circuit current
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
13) | Steady-State Short Circuit Current (Iac(t))
The r.m.s value of the symmetrical A.C component of the prospective short-circuit current at the “t” cycle
from the beginning of a short-circuit
14) | Symmetrical Short Circuit Breaking Current (Ib)
r.m.s value of an integral cycle of the symmetrical AC component of the available short circuit current at the
instant of contact separation of the first pole of a switching device
15) | Voltage factor “c”
Ratio between the equivalent voltage source and the nominal system voltage Un divided by 3^(1/2) .
The values are given in table as below.
The introduction of a voltage factor “c” is necessary for various reasons;.
- Voltage variations depending on time and place
- Changing of transformer taps
- Neglecting loads and capacitance by calculations
- The sub-transient behavior of generators and motors
| Nominal voltage Un |  | Voltage factor “c”
|  |  | Maximum short circuit currents C | Minimum short circuit currents C
| Low voltage, Un < 1000V |  | 1.05 | 0.95
| Medium voltage, 1000V ≤ Un ≤23000V |  | 1.1 | 1
| High voltage, Un > 23000V |  | 1.1 | 1
16) | Thermal equivalent short circuit current Ith
The r.m.s value of a current having the same thermal effect and the same duration as the actual
short circuit current, which may contain a DC component and may subside in time
17) | Ambient Temperature
The reference temperature considered for normal operation is based on ambient 45°C
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
1.4 | Electrical System Data
1.4.1 | Software
The computer software used to perform the short circuit calculation is ETAP.
(Electrical Transient Analyzer Program Ver 22.5.0)
This short circuit calculation report was calculated by the IEC 61363.
1.4.2 | System Requirement
Symmetrical and peak values of calculated short circuit currents shall be lower than the relevant
equipment design values in any case.
1.4.3 | Load data
Basic parameters, like voltage, power rating and absorbed power, are taken from project documents.
LV motors are dealt with individually in the calculation. And motors are dealt with constant power loads.
Static loads are included as constant impedance loads and dealt with as single equivalent static loads
on the each bus.
The entered voltage value is referred to equipment (for instance, Shore source: 6.6kV) voltage.
1.4.4 | Assumptions
1) Motor capacity is based on the SLD(Wiring Diagram) motor capacity
2) The load of motors was applied to LUMP LOAD.
The MV loads are referring to ELA (Electric Load Analysis).
3) The X/R ratio of 2-winding transformers are based on the specification sheet.

## CASE
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
1.4.5 | Description of Components
1) Generator
Ident |  | CAPACITY [kW/kVA] |  | Voltage [kV] | TYPE |  | Xd" [%] | Remark
MAIN GEN.1,2,3,4 |  | 2,500kW / 3,125 kVA |  | 0.45 | DIESEL ENGINE |  | 21
- Reference: YZJ2022-1487,8(240530)
2) Transformer data
Ident |  | CAPACITY [kW/kVA] |  | Voltage [kV] | Wiring |  | %Z | Remark
NO.1,2 AMP TR |  | 3600 |  | 6.6 / 0.45 | △ - △ |  | 8
B-TR |  | 3600 |  | 3.3 / 0.45 | △ - △ |  | 8
Reference: 2_240125 KD223091 For Approval DWG (For LS MARINE - YZJ2022-1487s, H.V TR）
3) Shore power
Ident |  | Voltage [kV] |  | Short Circuit Rating |  |  | X/R | Remark
Shore power |  | 6.6 |  | 182905kVAsc (16kAsc)* |  |  | 20
4) Motors data
Motor |  |  | kV | kW | PF (%) | Eff (%) | Ist/In (%) | Starting Method
BOW THRUSTER |  |  | 3.3 | 2500 | 84 | 96.5 |  | AUTO
MAIN L.O PUMP |  |  | 0.44 | 4384.1 | 85 | 95.1 |  | AUTO
- Reference: 2_240125 KD223091 For Approval DWG (For LS MARINE - YZJ2022-1487s, H.V TR
- Reference: M30270-600-001JS_A_ELECTRICAL LOAD ANALYSIS_2024.04.12
* Refer to IEC80005-1，4.7 and ETAP Typical.
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
2.0 | SHORT CIRCUIT CALCULATION
The calculation of maximum and minimum short-circuit currents is based on the following simplifications.
1) For the duration of the short circuit there is no change in the type of short circuit involved, that is, a
three-phase short circuit.
2) For the duration of the short circuit, there is no change in the network involved.
3) Arc resistances are not taken into account.
4) All line capacitances and shunt admittances and non-rotating loads, except those of the zero
sequence system, are neglected.
5) The ‘c’ factor was applied. (Max short circuit current: LV/MV/HV = 1.05/1.1/1.1; Min short circuit current:
LV/MV/HV = 0.95/1/1)
2.1 | Case Study
Case 1# AMP (Max short circuit current)
1) None of the generators are in operation (2,500kW/EA)
2) SHORE POWER is connected.
3) Bow thruster is not running.
4) Bustie CBs are open.
5) The load capacity was considered for the Load (4384.1 kW).
(-Reference: M30270-600-001JS_A_ELECTRICAL LOAD ANALYSIS_2024.04.12)
Case 2# AMP (Min short circuit current)
1) None of the generators are in operation (2,500kW/EA)
2) SHORE POWER is connected.
3) Bow thruster is not running.
4) Bustie CBs are open.
5) The load capacity was considered for the Load (0 kW).
(-Reference: M30270-600-001JS_A_ELECTRICAL LOAD ANALYSIS_2024.04.12)
Case 3# AMP+G1+G3 (Max short circuit current)
1) Generator 1 and Generator 3 are in operation (2,500kW/EA)
2) SHORE POWER is connected.
3) Bow thruster is not running.
4) Bustie CBs are open.
5) The load capacity was considered for the Load (4384.1 kW).
(-Reference: M30270-600-001JS_A_ELECTRICAL LOAD ANALYSIS_2024.04.12)
Case 4# AMP+G1+G3 (Min short circuit current)
1) Generator 1 and Generator 3 are in operation (2,500kW/EA)
2) SHORE POWER is connected.
3) Bow thruster is not running.
4) Bustie CBs are open.
5) The load capacity was considered for the Load (0 kW).
(-Reference: M30270-600-001JS_A_ELECTRICAL LOAD ANALYSIS_2024.04.12)

## Case1
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
2.2 | Result Summary
Case 1#
No. | BUS | Voltage [kV] | 0.5 Cycle Peak |  |  | 3 Cycle Peak |  |  | Remarks
|  |  | Ip[kA] | Iac(t)[kA] | PF | Ip[kA] | Iac(t)[kA] | PF
1 | 6.6kV AMP C/O PANEL | 6.6 | 47.2419 | 19.1452 | 0.09096 | 33.4491 | 18.9254 | 0.37738
2 | Cable Socket | 6.6 | 48.0367 | 19.2306 | 0.082098 | 34.8306 | 19.0116 | 0.33841
3 | 440V MSB BUS A | 0.44 | 139.8178 | 63.1231 | 0.17715 | 92.3261 | 60.5147 | 0.5796
4 | 440V MSB BUS B | 0.44 | 138.7178 | 62.968 | 0.18168 | 91.2896 | 60.3576 | 0.59428

## Case2
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
2.2 | Result Summary
Case 2#
No. | BUS | Voltage [kV] | 0.5 Cycle Peak |  |  | 3 Cycle Peak |  |  | Remarks
|  |  | Ip[kA] | Iac(t)[kA] | PF | Ip[kA] | Iac(t)[kA] | PF
1 | 6.6kV AMP C/O PANEL | 6.6 | 39.6336 | 15.68 | 0.072749 | 28.3302 | 15.68 | 0.35016
2 | Cable Socket | 6.6 | 40.371 | 15.7636 | 0.063506 | 29.595 | 15.7636 | 0.31005
3 | 440V MSB BUS A | 0.44 | 97.3189 | 41.3331 | 0.12517 | 64.2845 | 41.3331 | 0.54297
4 | 440V MSB BUS B | 0.44 | 96.3128 | 41.1794 | 0.13032 | 63.4232 | 41.1794 | 0.55869

## Case3
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
2.2 | Result Summary
Case 3#
No. | BUS | Voltage [kV] | 0.5 Cycle Peak |  |  | 3 Cycle Peak |  |  | Remarks
|  |  | Ip[kA] | Iac(t)[kA] | PF | Ip[kA] | Iac(t)[kA] | PF
1 | 6.6kV AMP C/O PANEL | 6.6 | 50.7638 | 20.3413 | 0.084185 | 36.1446 | 19.9649 | 0.35448
2 | Cable Socket | 6.6 | 51.5439 | 20.4257 | 0.076221 | 37.4909 | 20.0502 | 0.32084
3 | 440V MSB BUS A | 0.44 | 186.8795 | 80.8309 | 0.14861 | 120.881 | 74.7578 | 0.50713
4 | 440V MSB BUS B | 0.44 | 185.2608 | 80.6239 | 0.15342 | 119.0552 | 74.5696 | 0.5243

## Case4
SHORT CIRCUIT CURRENT CALCULATION
YZJ2022-1487 PROJECT
2.2 | Result Summary
Case 4#
No. | BUS | Voltage [kV] | 0.5 Cycle Peak |  |  | 3 Cycle Peak |  |  | Remarks
|  |  | Ip[kA] | Iac(t)[kA] | PF | Ip[kA] | Iac(t)[kA] | PF
1 | 6.6kV AMP C/O PANEL | 6.6 | 44.1676 | 17.4602 | 0.074526 | 31.0392 | 17.1947 | 0.35697
2 | Cable Socket | 6.6 | 44.8937 | 17.5423 | 0.066328 | 32.2893 | 17.2773 | 0.3207
3 | 440V MSB BUS A | 0.44 | 140.4153 | 57.6508 | 0.10823 | 90.5105 | 54.5297 | 0.46968
4 | 440V MSB BUS B | 0.44 | 138.9224 | 57.4461 | 0.11349 | 88.8883 | 54.3447 | 0.48846
ATTATCHMENT
A. Simulation Diagram : Iac (kA, rms) at t=0 cycle
B. Simulation Output Data